## Slide 1
MIDTERM
REVIEW
Physics-based simulation
→ data generation
→ machine learning
500
EnergyPlus cases
BPS5231 AI for Sustainable Building Design
Data Center Heatwave Resilience: A Machine-Learning Prediction Framework Based on EnergyPlus Data
Group C: Yang Baisong A0317341M Zhao Dingyi A0357194U

## Slide 2
1. Problem Description
Heatwaves create a compound risk for data centers
External stress
Higher outdoor temperature increases envelope heat gain; the simplified model also accounts for cooling-capacity degradation as heatwave intensity rises.
Internal stress
IT servers are 24/7 high-density heat sources; higher IT load increases the continuous heat-removal requirement.
Operational control
Cooling setpoint and available cooling capacity jointly determine whether the system can maintain a safe thermal environment.
DATA HALL
Thermal balance
& cooling capacity
Tmax
Risk hours
Cooling demand
Research question
Can physics-based simulations generate training data for ML models that rapidly predict thermal risk and cooling performance under different heatwave and operating conditions?

## Slide 3
2. Current Progress
1
DesignBuilder
Data Hall + plenums
Singapore weather
IT / lighting / equipment
2
EnergyPlus
Baseline reproduction
Manual capacity validation
Hourly outputs
3
Python Generator
IDF / EPW modification
LHS sampling
Automated simulation & extraction
4
500-case Dataset
500 case
21 columns
5 physical inputs
5
ML / EDA
Current stage
EDA → modelling
interpretation

## Slide 4
3. Data Generation Design
Five independent inputs (Latin Hypercube Sampling)
Heatwave intensity
0–10 °C
Duration
1–5 days
IT load
300–1000 W/m²
Capacity ratio
0.9–1.3
Cooling setpoint
20–27 °C
Capacity formulation
Qdesign = 68.089 × IT / 600
× Capacity Ratio
× (1 − 0.02 ΔT)
= Available Capacity
Heatwave timing
All heatwaves are centred on the baseline peak-cooling day (May 21): 1 day = May 21; 5 days = May 19–23.
Why this design?
Heatwave timing is controlled to prevent date from becoming a hidden variable. Cooling capacity scales with IT load, while a 2%/°C derating strengthens heatwave–HVAC coupling.

## Slide 5
6. EDA — Thermal Risk Distribution
Safe 360
Warning 75
Failure 65
Provisional thresholds for EDA: Safe <27°C; Warning 27–30°C; Failure ≥30°C.

## Slide 6
7. EDA — Key Relationships
Heatwave intensity ↑ generally raises risk
Capacity ratio ↑ generally suppresses risk
high intensity is most problematic when capacity margin is low.

## Slide 7
10. Data Quality Note
Extreme Tmax is a model failure state, not an operating temperature
65
≥30°C
40
≥40°C
25
≥50°C
Why runaway occurs
The model maintains continuous IT heat release. When heat generation persistently exceeds available cooling, the zone heat balance continues to raise the temperature.
Recommended ML treatment
Retain the raw data and add a Thermal_Runaway flag . These cases remain Failure in classification; Tmax regression can report both the full dataset and a non-runaway subset.

## Slide 8
11. Potential Method
Raw dataset
500 cases
5 physical inputs
Pre-processing
QC / labels
train-test split
Model training
Classification
Regression
Cross-validation
Evaluation
F1 / Recall
R² / MAE / RMSE
Interpretation
Feature importance
SHAP
Failure boundary
Candidate models
Logistic / Linear
Decision Tree
Random Forest
Gradient Boosting
XGBoost